## START HERE
Item | Value
Product | Industrial Fieldbook — Data-Center PDU / RPP — FREE PREVIEW
Version | V1
Coverage | PARTIAL — this preview shows a deliberate subset of manufacturers, families and attributes. Counts below are preview counts, not full product counts.
Manufacturers in the full product | 8
Manufacturers shown here | 3 (partial)
Families in the full product | 25
Specifications in the full product | 442
Evidence relationships in the full product | 442
Sources cited in the full product | 26
Sources checked | 2026-09-10 to 2026-09-10
What the full workbook adds | The complete family set, the full specification matrix across every well-covered attribute, the complete evidence chain with clickable sources, attribute coverage counts, and CSV/JSON exports.
UNKNOWN | Not established by the sources reviewed. Not a negative finding.
Contact | doug@industrialfieldbook.com

## PREVIEW FAMILY SCREEN
Family ID | Manufacturer | Family | Family name | Lifecycle status | Product type | Branch circuit monitoring | Output voltage | Rated kVA max | Transformer based | Input voltage
PF-010 | Eaton Corporation plc | Eaton PDI PowerHub 2 PDU | Eaton PDI PowerHub 2 PDU | CURRENT | Power distribution unit | yes (PDI WaveStar BCMS, factory-installed option) | 600/346, 575/332, 480/277, 415/240 or 208/120 V at 60 Hz | 1250 | yes | 600, 480 or 208 V at 60 Hz; 380-415 V at 50 Hz
PF-011 | Eaton Corporation plc | Eaton PDI PowerPak PDU | Eaton PDI PowerPak PDU | CURRENT | Power distribution unit | yes (BCMS, factory-installed option) | 600, 480 or 208/120 V at 60 Hz; 415/240 or 380/220 V at 50 Hz | 300 | yes | 600, 480 or 208 V at 60 Hz; 415 or 380 V at 50 Hz
PF-012 | Eaton Corporation plc | Eaton PDI PowerPak 2 PDU | Eaton PDI PowerPak 2 PDU | CURRENT | Modular power distribution unit | yes (BCMS, factory-installed option) | 600, 575, 480, or 208/120 V at 60 Hz; 575, 415/240, or 380/230 V at 50 Hz | 400 | yes | 600, 480 or 208 V at 60 Hz; 380-415 V at 50 Hz
PF-013 | Eaton Corporation plc | Eaton PDI PowerPak RPP | Eaton PDI PowerPak RPP | CURRENT | Remote power panel | yes (BCMS)
PF-014 | Eaton Corporation plc | Eaton Remote Power Panel | Eaton Remote Power Panel | DISCONTINUED | Remote power panel | yes | 208/120 V or 400 V, 3 phase 4 wire plus ground
PF-020 | Vertiv Holdings Co. | Vertiv Liebert PPC (400-1000 kVA) | Vertiv Liebert PPC (400-1000 kVA) | CURRENT - NEW GENERATION | Power conditioning and distribution cabinet |  | 208/120 V; 400/231 V; 415/240 V | 1000 | yes
PF-021 | Vertiv Holdings Co. | Vertiv Liebert PPC 400-800kVA (pre-2024 legacy models) | Vertiv Liebert PPC 400-800kVA (pre-2024 legacy models) | LEGACY | Power conditioning and distribution cabinet |  |  | 800 | yes
PF-022 | Vertiv Holdings Co. | Vertiv Liebert PPC 15-125kVA (pre-2024 legacy models) | Vertiv Liebert PPC 15-125kVA (pre-2024 legacy models) | LEGACY | Power conditioning and distribution cabinet |  |  | 125 | yes
PF-023 | Vertiv Holdings Co. | Vertiv Liebert RX Distribution Cabinet | Vertiv Liebert RX Distribution Cabinet | CURRENT | Remote power distribution cabinet | yes (option)
PF-024 | Vertiv Holdings Co. | Vertiv Liebert RXA Remote Power Panel | Vertiv Liebert RXA Remote Power Panel | CURRENT | Remote power panel
PF-050 | LayerZero Power Systems, Inc. | LayerZero ePanel SL Series (eRPP) | LayerZero ePanel SL Series (eRPP) | CURRENT | Remote power panel (eRPP) |  | 120/208 V |  |  | 120/208 V
PF-051 | LayerZero Power Systems, Inc. | LayerZero ePanel-2 (eRPP) | LayerZero ePanel-2 (eRPP) | CURRENT | Remote power panel (eRPP)
PF-052 | LayerZero Power Systems, Inc. | LayerZero eRPP-FSL (eRPP) | LayerZero eRPP-FSL (eRPP) | CURRENT | Remote power panel (eRPP)
PF-053 | LayerZero Power Systems, Inc. | LayerZero ePanel-HD Series (high-density eRPP) | LayerZero ePanel-HD Series (high-density eRPP) | CURRENT | High-density remote power panel (eRPP)
PF-054 | LayerZero Power Systems, Inc. | LayerZero eRDP Series (remote distribution panel) | LayerZero eRDP Series (remote distribution panel) | CURRENT | Remote distribution panel
PF-055 | LayerZero Power Systems, Inc. | LayerZero ePODs Series (PDU) | LayerZero ePODs Series (PDU) | CURRENT | Power distribution unit |  | 240/415 V and 120/208 V | 750 | yes (transformer-based subfeeds on the 480 V to 120/208 V model) | 480 V

## SAMPLE EVIDENCE CHAINS
Evidence ID | Family ID | Manufacturer | Attribute | Normalized value | Exact supported claim (as published by the source) | Evidence class | Source type | Primary vs third party | Confidence | Ambiguity / caveat | Source URL | Source title | Date checked
EV-0001 | PF-001 | ABB Ltd | app_colocation | yes | - **400-800 kVA** - Power distribution unit for 480V input to step down voltage to either 415/240V or 208/120V. Configurable with sub-feed distribution breakers. Most commonly deployed in colocation data centers. | VERIFIED_DIRECT | current product page | primary | High |  | https://electrification.us.abb.com/products/power-distribution-systems/trufit-pdu-50-800-kva | product page | 2026-09-10
EV-0002 | PF-001 | ABB Ltd | app_enterprise_dc | yes | - **50-300 kVA** \- Power distribution unit for 480V input to step down voltage to 208/120V. Configurable with sub-feed distribution breakers or 42-pole panelboards. Most commonly deployed in traditional enterprise data centers. | VERIFIED_DIRECT | current product page | primary | High |  | https://electrification.us.abb.com/products/power-distribution-systems/trufit-pdu-50-800-kva | product page | 2026-09-10
EV-0003 | PF-001 | ABB Ltd | app_hyperscale | yes | - **850 kVA and above** \- Power distribution unit for 480V input to step down voltage to either 415/240V. Configurable with sub-feed distribution breakers. Most commonly deployed in hyperscale data centers. For additional information, contact tech support or your local sales representative. | VERIFIED_DIRECT | current product page | primary | High |  | https://electrification.us.abb.com/products/power-distribution-systems/trufit-pdu-50-800-kva | product page | 2026-09-10
EV-0004 | PF-001 | ABB Ltd | branch_circuit_monitoring | yes | The TruFit PDU features ABB’s PowerView Pro , the company's first multifunctional PDU monitoring system to provide a truly holistic view of equipment health and performance. PowerView Pro combines revenue-grade branch or sub-feed metering with breaker status monitoring and integrated thermal monitoring. ABB’s integrated thermal monitoring automates traditional, manual thermography routines, continuously monitoring the temperature of input/output bolted connections. PowerView Pro ensures optimal efficiency and proactively identifies potential loosening connections. | VERIFIED_DIRECT | corporate press release | primary | High |  | https://new.abb.com/news/detail/108067/abb-trufit-power-distribution-unit-provides-rapid-space-saving-solution-for-data-centers | press release | 2026-09-10

## METHODOLOGY
Item | Value
Product | Industrial Fieldbook — Data-Center PDU / RPP — FREE PREVIEW
What this product is | A structured comparison of current product families in one industrial category. Every populated value is tied to a public source. Comparison rows are drawn from manufacturer product pages, technical documents and corporate disclosures that were archived and dated at build time.
What is in the commercial view and what is not | Only evidence rows classified VERIFIED_DIRECT (the value is stated on the cited source) or DERIVED_DETERMINISTIC (the value follows mechanically from stated facts by a recorded rule) are published. Rows classified as analytic inference, unresolved conflict or status-unclear are excluded, and the count of excluded rows is disclosed in the COVERAGE tab. Exclusion is disclosed, not hidden, and it is a quality signal: a claim that could not be tied to the source is not published.
UNKNOWN and NOT ESTABLISHED | An empty cell or the word UNKNOWN means the sources reviewed did not establish the fact. It does not mean the product lacks the capability, and it is not a negative finding. Missing data is left missing rather than filled by assumption.
Dates | Every evidence row carries the date its source was checked. The COVERAGE tab states the range of those dates. This is a dated snapshot, not a live feed.
What this product does not cover | It is not a price list, lead-time guide, availability feed or procurement recommendation. It does not establish engineering suitability for your application, approved-vendor status, warranty terms, service coverage, certificate scope beyond what the source states, or export eligibility. It does not rank suppliers.