## START HERE
Item | Value
Product | Industrial Fieldbook — UPS Battery Systems — FREE PREVIEW
Version | V1.1
Coverage | PARTIAL — this preview shows a deliberate subset of manufacturers, families and attributes. Counts below are preview counts, not full product counts.
Manufacturers in the full product | 6
Manufacturers shown here | 3 (partial)
Families in the full product | 9
Specifications in the full product | 158
Evidence relationships in the full product | 158
Sources cited in the full product | 19
Sources checked | 2026-09-10 to 2026-09-10
What the full workbook adds | The complete family set, the full specification matrix across every well-covered attribute, the complete evidence chain with clickable sources, attribute coverage counts, and CSV/JSON exports.
UNKNOWN | Not established by the sources reviewed. Not a negative finding.
Contact | doug@industrialfieldbook.com

## PREVIEW FAMILY SCREEN
Family ID | Manufacturer | Family | Family name | Chemistry | Dc voltage nominal | UPS compat | Physical | Runtime | UL 9540a | Env
UBF-001 | Vertiv Holdings Co. | Vertiv EnergyCore Li5 Lithium-Ion Battery Cabinet | Vertiv EnergyCore Li5 Lithium-Ion Battery Cabinet | LFP | 288 / 461 / 518 VDC | OEM-approved: most current and legacy 3-phase Vertiv UPS | 600x750x2000mm; 400/543/590 kg | 5-minute EOL runtime (optimized) | TESTED (4th edition) | Operating 20-30C; altitude 3000m
UBF-002 | Vertiv Holdings Co. | Vertiv EnergyCore Li7 Lithium-Ion Battery Cabinet | Vertiv EnergyCore Li7 Lithium-Ion Battery Cabinet | NMC | 304.5 / 486.4 / 516.8 VDC | OEM-approved: most current and legacy 3-phase Vertiv UPS | 600x750x2000mm; 350/475/495 kg | 7-minute EOL runtime (optimized) | TESTED (4th edition) | Operating 18-28C; altitude 2000m
UBF-006 | Mitsubishi Electric Corporation (MEPPI US) | Mitsubishi Electric BCL04-CB Lithium-Ion Battery Cabinet | Mitsubishi Electric BCL04-CB Lithium-Ion Battery Cabinet | LMO/NMC mix | 516.8 VDC (operating 435-571 VDC) | OEM-APPROVED: 1100B, 9900AEGIS, 9900B, SUMMIT, 9900CX, 9900D | 25.6 x 23.6 x 80.9 in; 1183 lb; top cable entry | 2-20 minute runtimes | (stated in datasheet certifications list) | Operating 18-28C; storage 0-40C
UBF-007 | Mitsubishi Electric Corporation (MEPPI US) | Mitsubishi Electric BCL04-CBA01 Lithium-Ion Battery Cabinet (for 1100B) | Mitsubishi Electric BCL04-CBA01 Lithium-Ion Battery Cabinet | NMC |  | OEM-INTEGRATED: 1100B (10-80 kVA) UPS |  | 2-20 minute runtimes
UBF-008 | ZincFive, Inc. | ZincFive BC Series UPS Battery Cabinets (nickel-zinc) | ZincFive BC Series UPS Battery Cabinets (nickel-zinc) | NICKEL_ZINC | 468/481/494/507 Vdc (36s/37s/38s/39s) | OEM-OFFERED: backward/forward MW-class UPS compatible | BC 2 cabinet 21 in width; ~1/3 lead-acid weight | BC 2-500 <5 min; others >5 min (up to 15); BC 2 AI sub-5 | TESTED (all models: YES) | Warranted to 35C; excursions to 50C

## SAMPLE EVIDENCE CHAINS
Evidence ID | Family ID | Manufacturer | Attribute | Normalized value | Exact supported claim (as published by the source) | Evidence class | Source type | Primary vs third party | Confidence | Ambiguity / caveat | Source URL | Source title | Date checked
EV-B0012 | UBF-001 | Vertiv Holdings Co. | bms | Integrated BMS: SoC/SoH real-time, cell-module-cabinet-facility | Advanced BMS with real-time SoC monitoring and SoH tracking; The Vertiv Battery Management System (BMS) provides ... visibility at every level including cell, module, cabinet, and facility | VERIFIED_DIRECT | product datasheet PDF (SL-71271 REV06) | Primary - manufacturer/OEM published | High |  | https://www.vertiv.com/4a3ae5/globalassets/shared/vertiv-energycore-battery-storage-system-data-sheet-sl-71271.pdf | Vertiv Group Corp. | 2026-09-10
EV-B0013 | UBF-001 | Vertiv Holdings Co. | cell_monitoring | cell / module / cabinet / facility level visibility | The Vertiv Battery Management System (BMS) provides secure, real-time visibility at every level including cell, module, cabinet, and facility | VERIFIED_DIRECT | product datasheet PDF (SL-71271 REV06) | Primary - manufacturer/OEM published | High |  | https://www.vertiv.com/4a3ae5/globalassets/shared/vertiv-energycore-battery-storage-system-data-sheet-sl-71271.pdf | Vertiv Group Corp. | 2026-09-10
EV-B0002 | UBF-001 | Vertiv Holdings Co. | chemistry | LFP | Cell Type ¦ Lithium-Iron Phosphate LFP Cylindrical Cell | VERIFIED_DIRECT | product datasheet PDF (SL-71271 REV06) | Primary - manufacturer/OEM published | High |  | https://www.vertiv.com/4a3ae5/globalassets/shared/vertiv-energycore-battery-storage-system-data-sheet-sl-71271.pdf | Vertiv Group Corp. | 2026-09-10
EV-B0014 | UBF-001 | Vertiv Holdings Co. | comms | Modbus TCP/IP, SNMP, Modbus RTU (RS-485) | Network Interfaces ¦ 100MB Ethernet supports Modbus TCP or SNMP. RS-485 supports Modbus RTU | VERIFIED_DIRECT | product datasheet PDF (SL-71271 REV06) | Primary - manufacturer/OEM published | High |  | https://www.vertiv.com/4a3ae5/globalassets/shared/vertiv-energycore-battery-storage-system-data-sheet-sl-71271.pdf | Vertiv Group Corp. | 2026-09-10

## METHODOLOGY
Item | Value
Product | Industrial Fieldbook — UPS Battery Systems — FREE PREVIEW
What this product is | A structured comparison of current product families in one industrial category. Every populated value is tied to a public source. Comparison rows are drawn from manufacturer product pages, technical documents and corporate disclosures that were archived and dated at build time.
What is in the commercial view and what is not | Only evidence rows classified VERIFIED_DIRECT (the value is stated on the cited source) or DERIVED_DETERMINISTIC (the value follows mechanically from stated facts by a recorded rule) are published. Rows classified as analytic inference, unresolved conflict or status-unclear are excluded, and the count of excluded rows is disclosed in the COVERAGE tab. Exclusion is disclosed, not hidden, and it is a quality signal: a claim that could not be tied to the source is not published.
UNKNOWN and NOT ESTABLISHED | An empty cell or the word UNKNOWN means the sources reviewed did not establish the fact. It does not mean the product lacks the capability, and it is not a negative finding. Missing data is left missing rather than filled by assumption.
Dates | Every evidence row carries the date its source was checked. The COVERAGE tab states the range of those dates. This is a dated snapshot, not a live feed.
What this product does not cover | It is not a price list, lead-time guide, availability feed or procurement recommendation. It does not establish engineering suitability for your application, approved-vendor status, warranty terms, service coverage, certificate scope beyond what the source states, or export eligibility. It does not rank suppliers.